fire extinguisher selection guide

Extinguishers should be selected according to the types of firelikely to occur, i.e.:

Class A - solids such as paper, wood and textiles.

Class B - liquids such as petrol, diesel, solvents and alcohol.

Class C - gases such as propane and acetylene.

Class D - metals such as magnesium and sodium.

Class F - cooking oil.

Fires involving live electrical equipment.

Extinguisher ratings

Each extinguisher has a rating to indicate its extinguishing abilities and the class of fire for which the rating applies, e.g. a standard 9 litre water extinguisher has a 13A rating.

Numbers by area

The minimum provision for A-rated extinguishers is one extinguisher with a rating of 13A for every 200m2 of floor space. But in any case you should normally have at least two of these per floor, unless the floor space is less than 90m2, in which case you can justify only one.

For larger floor areas you can calculate the Class A provision by multiplying the floor area of a storey by 0.065. For example, a floor area of 400 m2 would have a rating of 26A (400 x 0.065 = 26), e.g. 2 x 13A rated extinguishers.

Where there are other classes of fire risk, you should position an extinguisher of the right type within easy reach.

Other considerations

When determining the numbers required the floor area is just one factor. You should also consider the layout of the building and travel distances.

The previous thinking was that the maximum distance of travel in the workplace to an extinguisher ought not to exceed 30 metres. But whilst the 30-metre rule still applies to Class A fires, i.e. those put out by water and AFFF extinguishers, the recommended maximum distance for other classifications of extinguisher has been reduced (ref. BS5306-8). For Class B and Class F fires and those involving electrical equipment, the recommended maximum distance is now ten metres.

When deciding where to position fire extinguishers, select locations on escape routes, close to exits from rooms, floors or final exits from the building. Ideally you should avoid having to pass through multiple doors to reach an extinguisher.

For extinguishers relating to particular hazards, position them close to the hazard but where there is a clear escape.

Ideally the location you choose for your extinguishers should be close to a manual alarm call point so that the alarm can be raised prior to any attempt to fight a fire.

In summary

Often, once the maximum travel distances and other locational factors have been taken into account, the number of extinguishers required will easily exceed the minimum number required according to the floor area.

It is good practice to group extinguishers so that there is a choice of types at one fire point. For example, it would be usual to position a water or foam extinguisher (A-rated) together with a carbon dioxide (best for electrical fires) at each fire point.